## Consultation
SECOND TARGETED STAKEHOLDER CONSULTATION
GMP Revision on Annex 1 Manufacture of Sterile Products
1. Introduction
The current annex 1 is being reviewed to better ensure the sterility of medicinal products placed on the market for the benefits of patients. The revision was notably necessary to facilitate implementation of the principles of relevant ICH guidelines, to extend the underlying concepts to include new areas of technology and processing not previously covered and also to clarify areas that have been highlighted as ambiguous due to the age of the document. In order to maintain the global alignment of standards, achieving at the same time assurance for the highest quality, the Annex 1 Working Group (WG) is made of experts from the European Commission, the World Health Organisation (WHO) and the Pharmaceutical Inspection Co-operation Scheme (PIC/S). A first draft of the revised Annex 1 was published for public consultation from 20 December 2017 to 20 March 2018. Following the contribution of about 140 stakeholders and after processing more than 6200 comments the WG issued a revised document, version 12, in December 2019. Due to widespread interest from industry following the first public publication of the Annex 1, it was found necessary to engage with stakeholders in a second targeted consultation on the updated draft guidance, version 12. The second consultation aims at collecting experience from the sectors on certain changes proposed and concerns raised. The associations representing the sectors were therefore contacted and are expected to provide a contribution. The draft guideline of version 12 provided has been formatted with prescribed line and page numbers. To submit feedback, please provide it exclusively using this dedicated template below.
2. Scope of the consultation This second consultation is intended to be focused and limited to paragraphs that raised concerns or were changed more significantly, as identified below.
2.1. Feedback on the concerns raised by stakeholders
| Qualification & requalification of cleanroom | from § 4.25 to 4.35
| Handling of water systems | from § 6.7 to 6.15
| Integrity testing of large volume parenteral container | § 8.21
| Handling of sterilizing filter including pre-use post sterilization integrity testing (Pupsit) | § 8.88 and 8.95 & 8.96
| Handling of lyophiliser | from § 8.110 to 8.113
| Sterility testing | § 10.6 & 10.7
2.2. Sections and/or paragraphs which were substantively modified
| Definition and handling of barriers systems including disinfection/decontamination | from § 4.18 to 4.24
| Handling of gas filters | from § 6.18 to 6.20 and 8.89 & 8.90
| Personnel qualification & gowning | § 7.5 & 7.6 and from 7.14 to 7.16
| Aseptic production | from § 8.11 to 8.19
| Moist heat sterilisation | from § 8.54 to 8.65
| Personnel monitoring | § 9.32 & 9.33
| Aseptic process stimulation (APS) | § 9.34 & 9.40 & 9.47
| Quality control | § 10.1
2.3. Other significant comments
All document
3. Name and contact details of the reviewing organisation
EFPIA/Vaccines Europe
4. Comments
Please write your comments using the spreadsheet below
Line number (s) | Comments | Suggested text | Justification
GENERAL COMMENT 1 | EFPIA note the second paragraph of the Scope statement. However, EFPIA still believe there are examples within the document that are too prescriptive and where the use of risk assessments and/or the Contamination Control Strategy (CCS) would add value to the document. Specific examples include 4.19, 4.24 4.36, 4.38, 9.31
GENERAL COMMENT 2 | Some parts of the document are confusing because it does not always consider the different approaches that are used with the different specific technologies (e.g. Isolators/Closed RABS/Open RABS). Specific examples include 4.18, 4.23, 5.5, 9.27 9.40
GENERAL COMMENT 3 | The document includes a number of 'guidance values' which we do not believe add value, and in some cases can cause mis-interpretation by inspectors and/or industry as a requirement. Specific examples include 4.31, 4.32. 8.58, 8.59
OUT OF SCOPE (OOS) COMMENTS | We have included some important comments at the end of the list that relate to sections of the document that were NOT included in the EMA request. All such comments are identified in the line number column with the addition of '(OOS)'. These comments include major discrepancies. for example sections dealing with Blow Fill Seal (BFS) and Form Fill Seal (FFS).
322-325 | 4.18 discusses that Isolators and RABs should protect the grade A area. When providing technologies to support transfer of materials into the barrier, Rapid transfer technologies and transfer isolators are cited and are very good for some applications but there are other technologies, especially for RABs which should be acknowledged, such as No Touch Transfer Systems (NTT), Small transfer slots, etc. These are well suited for the components such as tubs of pre-filled syringes. Propose eliminating the term preferably as it prescribes only a few technologies, and state utilizing appropriately qualified technologies including....... and expanding the list of other technologies. 4.18 does not consider Open RABS. The document should differentiate open/closed RABS as one requirement may not fit both, for example the transfer of materials from grade B to grade A | Isolator or RABS technologies, and the associated processes, should be designed to provide protection of the Grade A environment. The entry of materials during processing (and after decontamination) should be minimized and preferably utilize validated transfer technologies such as supported by: i. Rapid transfer technologies (RTT) or transfer isolators for Isolators. ii. No touch transfer systems (NTT). iii. Transfer slots or openings with unbagging for RABs For conventional aseptic lines and open RABs, material transfers from Grade B to Grade A can occur through open door interventions without the use of transfer isolator/rapid transfer technologies although such transfers should be kept to an absolute minimum | See general comment 2. Need to identify additional transfer technologies for each type of barrier as there are others which are appropriate for different types of equipment and components. Requirement written from an isolator perspective. Open RABS systems are accepted as per the document and they will not have rapid transfer technologies in the same sense as isolators.
327-330 | 4.19 is a good example where the role of the Contamination Control Strategy can be highlighted to document the critical risks | "…the risk factors, as outlined in the Risk Assemment of the CCS and associated with the manufacturing operations and the operations conducted within the critical zone." | See general section 1
332 | 4.20 second sentence mentions "In closed isolator systems where airflow may not be unidirectional, it should provide Grade A conditions and be demonstrated to provide adequate protection for exposed products during processing." The use of the words "Grade A conditions" here implies unidirectional airflow. Recommend changing to “air supply should meet Grade A Microbial and particulate limits” | ….."In closed isolator systems where airflow may not be unidirectional, air supply should meet Grade A Microbial and particulate limits and be demonstrated to provide adequate protection for exposed products during processing." | The prior version had the following : Using the word “conditions” here could imply unidirectional airflow. "Grade A conditions" needs to be replaced by an adequate or other term or defined in the glossary.
347 | 4.22 This section should clarify whether background environment of a closed isolator should correspond to a minimum of Grade D for manufacturing and sterility test isolators, or just for manufacturing isolators. EFPIA propose it should refer only to manufacturing isolators. | "The background environment of a closed isolator used for manufacturing should correspond to a minimum of Grade D." | It is a company risk whether or not to place a closed isolator used for sterility testing in a background environment less than a grade D
353 | 4.23 includes requirements for integrity testing and/or inspection of the glove systems at a specific frequency. Such inspection or testing should be in line with the CCS. There is currently not enough differentiation between open RABS and Isolator glove systems | …."The testing and inspection of gloves should be performed at periods defined within the CCS," | See general section 1. The use of QRM is clearly stated in the Scope of the document and is also stated to be applicable in its entirety throughout the document. Using QRM principles should drive the frequency of inspection/ integrity testing
365 - 381 | 4.24 Processes for decontaminating RABS and isolator systems may be both automated and manual in nature. Manual methods will not have defined cycle parameters 4.24 ii includes the statement "For RABS System, disinfection should include the routine application of a sporicidal agent.." The wording "routine" implies that this for example should be done daily or weekly. Manual cleaning with sporicidal agent will dry out hypalon and similar materials and might cause other risk as excessive particle generation. VHP decontamination is also not possible to perform in open RABS that frequently since the system is not installed with VHP decontamination and thus the VHP decontamination has to include Grade B. The same applies to Section 4.36, (although out of scope for this round of commenting), as it also mentions the use of sporicidal agents and disinfection rotation There are numerous studies showing no added value of rotational use of more than one type of disinfectant. Furthermore, confirmatory studies mentioned in 4.37 must anyway demonstrate appropriateness of the disinfection method, and this can be something that can easily be incorporated into the CCS | "4.24 For RABS and isolator systems, decontamination methods should be validated and controlled." "ii For RABS systems, the disinfection should be based upon the results of the environmental monitoring programme using a method that has been validated and demonstrated to robustly disinfect the interior and ensure a suitable environment for aseptic processing." | Inclusion of both manual and automated methods for decontamination See general comment 1. The frequency of biocidal rotation should be based on cleanroom performance that is derived from the output of environmental monitoring programme and CCS. Unnecessary use of sporicidal agents might increase risk for material deterioration and chemical residues in grade A. There are scientific studies that demonstrate that mechanical cleaning of a surface can produce about 3 log reduction of spore forming bacteria. This is the same level of reduction that can be seen with many sporicidal agents. The requirement should reflect the result that should be achieved. See general comment 1. Section 4.24 (and 4.36 and 4.38 out of commenting scope) is an example where the use of QRM (and documented in the CCS) is well-suited to describe the choice of disinfectants, disinfectant specifications (including sterility or bioburden requirements), frequency of use, and any rotation policies, to reflect the criticality of activities in different grades of cleanroom depending upon the nature of the work being performed and potential risk to the products or damage to the equipment
392-394 | 4.26 Cleanrooms and clean air devices (rather than equipment) should be qualified using methodology in accordance with the requirements of Annex 15. Cleanroom qualification (including classification) should be clearly differentiated from operational environmental monitoring. | "Cleanrooms and clean air devices should be qualified using methodology in accordance with the requirements of Annex 15. Reference to suitable methodology for qualification and classification can be found in the ISO 14644 series of standards and other ISO standards where applicable . Cleanroom qualification (including classification) should be clearly differentiated from operational environmental monitoring." | It is important to ensure that there is a reference to ISO 14644
424 | 4.29 Currently gives the option to include 1 μm particulates, but no limits are provided in Table 1, and gives additional complexity that counters the Clause 4.4 in ISO14644-1. We recommend that the reference to 1 μm is removed. | "For cleanroom classification, the airborne particulates equal to or greater than 0.5 and 5 µm should be measured. For Grade A zone and Grade B at rest, classification should include measurement of particles equal to or greater than 0.5 µm. however, measurement using a second, larger particle size, e.g. 1 µm in accordance with ISO 14644 may be considered. This measurement should be performed both at rest and in operation. The maximum permitted airborne particulate concentration for each grade is given in Table 1." | We do not have historical data nor is there scientific justification to introduce e second measurement at rest in Grade A/B. The suggested particle size is not aligned with ISO 14644-1 4.4 requirement that each larger particle size be at leas 1.5 times the diamter of the smaller particle size. What situations would warrant a considering second threshold for Grade A or B? If the 1μm particle size is required - no limits are provided - do the ISO 14644 Table 1 limits (832) apply?. Without specific guidance, conservatively the default would be to apply the 0.5 μm limits to the 1μm particle size, but this is already captured in the 0.5 μm measurement providing no additional value. Additionally, Table 6 (line 1887) and other references throughout the annex are to ≥5 μm.
446 and 461 | 4.31 The correct term for clean room is "cleanroom". This should be checked throughout the document 4.31 i) gives definitions of "at rest". We believe the definition could be enhanced (see suggested text). 4.31 ii) gives definitions of "in operation". We believe the definition could be enhanced (see suggested text). The term qualification is more correct than certification when discussing "in Operation" state. 4.31 iii) gives guidance values for "clean up" period. We believe that guidance values do not add any value to the document. The requirement to have a clean up period is excessive for grade C/D where non critical activities are performed in these classes. The clean up period is not applicable for Grade A (UDAF!). | Cleanroom qualification should be carried out in the “at rest” and “in operation” states. i) The definition of “at rest” state is the condition whereby the installation of all the utilities is complete including any functioning HVAC, with the fixed permanent manufacturing equipment installed as specified and standing by for operation, without personnel in the room. ii) The definition of “in operation” state is the condition where the installation of the cleanroom is complete, the HVAC system fully operational, equipment installed and functioning in the manufacturer’s defined operating mode with the expected number of personnel present performing or simulating routine operational work. In operation qualification may be performed during simulated operations or during aseptic process simulations (where worst case simulation is required). iii) The particulate limits given in Table 1 above for the “at rest” state should be achieved after a “clean up” period on completion of operations. The "clean up" period should be determined during the classification of the rooms (guidance value of 15 to 20 minutes). | i) The term "Main" can have various meanings. Requesting clarifications so it is clear the equipment that is expected. Typically "fixed permanent" would be clearer and reflect this is your major installed equipment. ii) The term "qualification" is more correct than "certification" when discussing "in Operation" state. General comment 3. iii) The requirement for "Clean up" time should not be mandatory for low risk grades (Grade D and Grade C) were low risk activities take place and no risk to product quality impact.. It should also be noted that this is not applicable for Grade A (UDAF!).
463 - 470 | 4.32 Provides guidance values for theaire speed of unidirectional airflow systems. It is recommended to remove all such guidance values from the document as they add no value and can be misinterpreted by regulators and industry alike. | ......The speed of air supplied by unidirectional airflow systems should be clearly justified in the qualification protocol including the location for air speed measurement and supported by a risk-based approach. Airflow visualization studies should correlate with the air speed measurement location. | See general comment 1: The defined range of air speed should not be applied to all process configurations in Grade A including Barrier Technologies. The possibility to scientifically justify in the CCS other practices will help to ensure no multiple interpretations of the 'guidance values' by both regulatory and industry. See general comment 3. We recommend to remove the guidance range as it is based on a single configuration from a 50 year old study for the US military (US Military dropped this guidance c. 1987) and should not be applied arbitrarily to all configurations possible within a Grade A zone. Although stated as a guidance value, many firms experience with audits that inspectors are not treating this as a guidance value, even when there are supporting AFPT to support the velocities in use.
471 - 492 | 4.33 Microbial load is the more common term than microbial concentration 4.33 includes the requirements for the number of sampling locations including the results of the classification, air visualization studies and knowledge of the process and operations to be performed in the area. However, air visualisation studies are not necessary for grade C and D.(also true for section 4.15) 4.33 Note 1: mentions the methods indicated for a specific Grade in the table that should be used for qualifying the area of that specific | 4.33 The microbial load of the cleanrooms should be determined as part of the cleanroom qualification. The number of sampling locations should be based on a documented risk assessment, including the results of the classification, knowledge of the process and operations to be performed in the area, and the air visualization studies (mandatory for Grade A and B, and at grades C and D interfaces as a minimum unless directed by the CCS). The maximum recommended limits for microbial contamination during qualification for each grade are given in Table 2. Qualification should include both at rest and in operation states. Note 1: All methods (e.g. air sample/settle plates/contact plates ) should be used for qualifying the area of that specific Grade. If one of the methods is not used, or alternative methods are used, the approach taken should be appropriately justified. | See general section 1. Air visualization studies should be supportive only for Grades A and B cleanrooms. For Grades C and D only results of qualification and risk analysis should be supportive and documented as part of the Contamination Control Strategy i.e. For grades C and D , airflow visualisation studies at interfaces as a minimum, unless directed by the CCS. Please also consider the 4.15 Out of scope wording. to ensure consistency. The qualification methods should be flexible to allow future new technologies to be introduced.
494 - 513 | 4.34 Table 3 defines the minimum test requirements for the requalification of cleanrooms. Some name of tests should be replaced to ensure they match .ISO terminology and section 4.27 4.34 States that the requalification of cleanrooms and clean air equipment should be carried out periodically according to the frequency of either 6 or 12 months as indicated in lines 501 and 502. 4.34 Add a footnote to table 3 to indicate that air pressure difference can only be verified when there is a physical barrier between rooms | "Integrity Test of Terminal Filters" should be replaced by "Terminal Filter Leakage Testing" and "Air volume measurement" should be replaced by "Airflow Rate" "4.34 Cleanrooms should be requalified periodically and after changes to equipment, facility, or processes based on the principles of QRM. The rationale for the frequency of requalification should be documented. " | Harmonization with ISO 14644 Part 3 and consistency with Section 4.27 NOTES : Retain Table 3 - but remove the first column as this is related to EMPQ and make changes per comments in the justification section. Changes to Table 3: -The first column in table 3 should be removed. This section focuses on cleanroom and clean device equipment. 4.26 states that cleanroom qualification is separate from environmental monitoring. The EM program provides assurance of continuance of the qualified state where there have been no modifications to room, equipment or procedure and aspects of the program are addressed elsewhere in the annex. It would be better to separate the two to provide clarity. To achieve this, 4.33 should be moved to section 9 – between 9.4 and 9.5 - Add an asterisk (*) in column ""Integrity Test of Terminal Filters"" of Table 3 for Grade B, C, and D areas which will allow less frequent testing of terminal filters if supported by scientific justification documented in the CCS. - Where continuous monitoring exists, you should be able to extend your frequency of periodic testing. - Remove the airflow pressure differential as this is continuously monitored. - Measurement of airflow volume is only required for non-unidirectional air flow per ISO 14644-2 Table NA.1"
514 | 4.35 should include personnel comfort to minimize shedding | "Other characteristics, such as temperature and relative humidity, should be controlled within ranges that align with product/processing/personnel comfort requirements and support maintenance of defined cleanliness standards (e.g. Grade A or B)." | Personnel comfort is an important element to reduce shedding
633 - 638 | 6.7 Not all water systems require pyrogen control (e.g. Purified Water) therefore this would not be a universal attribute that would be required to be controlled. As such systems are not sterile and will harbour microorganisms, but these should be controlled to a level that does not exceed monograph requirements for the given water type. Suggested text is more line with Paragraph. 6.8 6.7 states that the criteria listed should be used to "prevent" biofilms. Prevention of biofilms isn't really possible. "Minimize" is the more appropriate term, as used in requirements 6.9 and 6.12 on the same topic. | "Water treatment plant and distribution systems should be designed (e.g. sloping of piping to provide complete drainage and the avoidance of dead legs), constructed and maintained to minimize the risk of particulates, microorganisms, pyrogens (if applicable) and formation of biofilms to ensure a reliable source of water of an appropriate quality. Where filters are included in the system, special attention should be given to the monitoring and maintenance of these filters. Water produced should comply with the current monograph of the relevant Pharmacopeia." | Water treatment plants in general are not able to be fully drained for all purification steps. Conservation of systems should also be an option. Dead-legs according to requirements stated in the Glossary list cannot always be obtained in water systems. Not all water systems require pyrogen control (e.g. Purified Water) therefore this would not be a universal attribute that would be required to be controlled. As such systems are not sterile and will harbour microorganisms, but these should be controlled to a level that does not exceed monograph requirements for the given water type. Suggested text is more line with Paragraph. 6.8 Prevention of biofilms isn't really possible, particularly in the early parts of generation systems, which are in the scope of this statement. Minimizing them throughout the water system is the more appropriate requirement.
640 - 641 | 6.7 states that "Water systems should be qualified to maintain the appropriate levels of physical, chemical and…." but the term should be validated in this context | Water systems should be qualified validated to maintain the appropriate levels of physical, chemical and………. | The complete lifecycle of a water system refers to validation (qualification is only a part of it) see USP <1231>
643-644 | 6.9 This section should only be applied to water distribution systems. Some water generation steps may not remain turbulent due to how they operate or due to the presence of Chlorine. | "Water flow should remain turbulent through the pipes in water distribution systems to minimize the risk of microbial adhesion, and subsequent biofilm formation." | Some portions of water generation systems are not turbulent and do not need to be turbulent due to how the unit operations function.
646-651 | 6.10 We often see inspectors apply the example temperature of 70C as an absolute requirement instead of accepting other strategies. Please add other examples of effective microbial control strategies, such as cold systems with regular hot water sanitization or ozone. | Reword to ". . . Of microbial growth (for example by constant circulation at a temperature above 70C, or by constant circulation at a cooler temperature with regular sanitization above 70C or with ozone). Where the . . ." | See general section 3. There are many proven microbial control strategies that can be used to maintain WFI systems. This statement should not unintentionally restrict the options available.
653-655 | 6.11 discusses the requirement for sterilization of WFI vent filters. WFI systems, though they are required to be very clean, are not required to be sterile. The statement to sterilize these filters should be removed. There is no scientific justification that requires installation of a sterile vent filter on a non-sterile system. | ". . .bacteria retentive vent filters, the filters should be sanitised and the integrity of the filters should be tested before and after use." | WFI systems, though the filters are required to be very clean, they are not required to be sterile. The integrity testing of the filters could be written more generally to account for different water systems.
657-661 | 6.12 discusses minimizing biofilm formation in water systems (both generation and distribution systems seem to be in scope based on the wording) by periodically sterilizing, disinfecting, or regenerating the systems. Some of these items are specific to generation systems (regeneration). Sterilization of water systems is not required to reduce the risk of biofilm formation in water generation or distribution systems. Sanitization with hot water or ozone is very effective at reducing the risk of biofilm. 6.12 Due to the delay in obtaining microbial counts after sampling following disinfection/regeneration, the continuous nature of WFI production and the need to return promptly to production after a shutdown, please consider allowing return to use after confirming acceptability of all parameters except microbial count. The WFI should be able to be returned to use at risk pending the microbial count if justified by risk assessment. | 6.12 To minimize the risk of biofilm formation, sterilization or disinfection or regeneration of water systems should be carried out according to a predetermined schedule and when microbial counts exceed action limits. It should be evaluated if a non-routine sanitisation, disinfection or regeneration is needed in case of exceeded microbial action limits. Disinfection of a water system with chemicals should be followed by a validated rinsing/flushing procedure. Water should be tested after disinfection/regeneration. The results should be approved before the water system is returned to use. The water system may be returned for use at risk pending microbial test results if justified by risk assessment." | Hot water sanitization and ozone are very effective at minimizing biofilm formation. Sterilization is difficult to perform on WFI systems, is dangerous to perform, and is unnecessary. When exceeding action limit for microbial counts - it does not always makes sence to perform a sanitisation, disinfection or regeneration. Sample data will occur 5-7 days after the exceed of the action limit so the value of this action might be limited. If there is a good history of the water system returning to baseline state after a disinfection/regeneration, releasing the water system at risk pending micro results poses little risk.
663-665 | 6.13 The alert levels can be based on both the qualification data and/or a review of the ongoing monitoring data 6.13 part iii requires sampling at the end of the distribution loop. Sampling at this location is not necessary. Microbial samples from this location do not represent the points where the water is actually used in production. Chemistry of water systems is considered to be evenly mixed, so a sample that represents the distribution loop can be collected anywhere in the distribution loop or measured with online instrumentation installed anywhere in the distribution loop. Sampling at this location is especially unnecessary non-WFI systems. | Regular ongoing chemical and microbial monitoring of water systems should be performed. Alert levels should be based on the qualification data and or a review of ongoing monitoring data that will identify an adverse trend in system performance. Suggest that point iii) is combined with point ii) and reworded as follows: "sample plans are based on a documented risk analysis that consider the potential worst case sampling locations and should ensure that at least one representative microbial sample of the distribution system is included every day that the WFI is used." | Improved clarity To mandate sampling the end of the distribution loop each day water is used is an unnecessary waste of resource for WFI and especially purified water systems. Most sample points at the end of the distribution loops will be in water plant rooms (e.g. before tank return) and the microbial result from this point is irrelevant to the real critical points of use where water is used in cleaning or in product makeup. Water systems will have online TOC and conductivity meters which will continually show the chemical purity, so it is just microbial quality being required and as stated previously this can vary dramatically from points of use, based on what is happening at the point. Sample plans should be risk based and include key points of use more often than return to tank.
758 | 7.5: The last sentance of section 7.5 states that "The unsupervised access to Grade A zone and Grade B areas where aseptic operations are or will be conducted should be restricted to appropriately qualified personnel, who have passed the gowning assessment and have participated in a successful aseptic process simulation (APS). There are people working in grade B areas that are not involved with the actual filling operation or have access to grade A. Inclusion of such operators in an APS should be done based upon the criticality of their job roles. This could be be documented in the CCS. | ...."The unsupervised access to Grade A zone and Grade B areas where aseptic operations are or will be conducted should be restricted to appropriately qualified personnel, who have passed the gowning assessment, and have participated in a successful aseptic process simulation (APS). The unsupervised access to Grade A zones should be restricted to the personnel who participated in a successful aseptic process simulation (APS)." | All the personnel working in Grade B are not always involved in manufacturing operation or other activities that involve ingress in Grade A or access to process or direct or indirect contact to the process or the product.
768-773 | 7.6 .....states that "If needed in exceptional cases, manufacturers should establish written procedures outlining the process by which unqualified personnel are brought into the Grade B and A areas. Access by these persons should be assessed and recorded in accordance with the PQS. An authorized person from the manufacturer should supervise the unqualified personnel during their activities and should assess the impact of these activities on the cleanliness of the area." In order to clearly point out the manufacturer's responsibility to supervise unqualified personnel and to document and evaluate the access to Grade A/B areas the following wording is proposed | ...." If needed in exceptional cases, manufacturers should establish written procedures outlining the process by which unqualified personnel are brought into the Grade B and A areas. An authorized person from the manufacturer should supervise the unqualified personnel during their activities. Access by these persons should be assessed concerning the impact of these activities and recorded in accordance with the PQS and should assess the impact of these activities on the cleanliness of the area." | Changed sequence of tasks and responsibilities of the manufacturer for a more practical wording.
831-832 | 7.14 I Garments should be packed and folded in such a way as to allow operators to gown without contacting the outer surface of the garment. The suggested text in the next column should be sufficient, and would take into consideration cases like: low part of the garment touched, but then is covered by an overboot | "Garments should be packed and folded in such a way as to allow operators to gown with contact to the outer surfaces of the garment reduced to a minimum." | The wording of the document needs to be practical
845 | 7.15 reference to changing rooms directly leading to Grade C should be deleted. | "Outdoor clothing (other than personal underwear) should not be brought into changing rooms leading directly to Grade B and C cleanrooms. Facility suits, covering the full length of the arms and the legs, and socks covering the feet, should be worn before entry to change rooms for Grades B. Facility suits and socks should not present a risk of contamination to the gowning area, processes or cleanrooms. The same controls should be applied to Grade C changing unless the contamination control strategy determines otherwise. " | The full covering is not necessarily needed for grade C changing rooms, if environmental monitoring data proves that procedure works and the specific grade C environment activities are not exposed to unnecessary risk . For example, for Grade C operations supporting isolator loading , BFS operations the CCS may deem that there is a risk to the operations due to clothing being exposed in the Grade c change room and therefore the CCS will conclude that additional precautions during gowning must be implemented.
853 | 7.16 The maximum duration of each garment should be defined as part of the qualification. | 7.16 The maximum duration of each protective garment should be defined as part of the qualification. | The use of the wording "protective garment" helps clarify the requirement.
932 | 8.11 Table 5 some examples of operations are missing. | In Table 5 add: Grade A add Loading and unloading of a lyophiliser Grade A rewording of Removal, cooling and transport of unprotected (e.g. with no packaging) items from sterilizers. Grade C add Filling of terminally sterilized product Grade D rewording "Assembly of closed and sterilized SUS using sterile connection devices. | Some key examples are missing.
940 | 8.12 I should indicate that for isolators, sterilised contact parts are placed into the open isolator with subsequent decontamination….. or it should clarify that you can sterilize these parts and transport into the closed isolator although the majority of Industry isolators are NOT set up to do this. | "i. All product and component contact equipment should be sterilized prior to use. When working with isolators, such sterilised equipment should be transferred into the isolator with subsequent decontamination." | Isolators are not subjected to a `sterilisation process but to a decontamination process. Therefore the section 8.12 should indicate that indirect contact parts are steam sterilized or decontaminated and placed into the open isolator prior to decontamination….. Or better request a clarification as you can sterilize these parts and transport into the isolator that is closed..... though the majority of Industry isolators are not set up to do this.
950-951 | "8.13 The unwrapping, assembly and preparation of sterilized equipment, components and ancillary items and the preparation and filling of the sterile product should be treated as an aseptic process and performed in a Grade A zone with a Grade B background." Preparation of product that is later sterile filtered before filling does not have to occur under grade A with grade B background. This is not in accordance with table 5. It is therefore proposed to remove the last sentence of this paragraph "Where an isolator or RABS is used, the background should be in accordance with paragraphs 4.21 & 4.22." | "8.13 The unwrapping, assembly and preparation of sterilized equipment, components and ancillary items and the filling of the sterile product should be treated as an aseptic process and performed in a Grade A zone with a Grade B background. Where an Where an isolator or RABS is used, the background should be in accordance with paragraphs 4.21 & 4.22." | Text provides better accuracy and clarity.
1216 | 8.54 The description relating to moist sterilisation is confusing and requires clarity. | 8.54 Steam is used for the sterilization of porous loads (porous items and surface sterilisation of hard goods), Sterilization in Place processes (SIP) as well as fluids loads (e.g. product). In a steam sterilization process, the critical parameters are Temperature, Pressure and process time in order to ensure saturated steam is being utilized for the duration of the cycle to achieve sterilization. Other alternative sterilization methods could be used for products that cannot support high temperatures (e.g.: Blow Fill and Seal containers, plastic bags etc.) such as for example those based on Superheated water (Immersion Cycles). In this case temperature, time and pressure, are also critical parameters in order to avoid boiling water and to be sure that the containers are not deformed by pressure decompensation along all the process. | The proposed text provides clarity and scientifically correct guidance
1230-1233 | 8.55 For porous cycles (hard goods) time, temperature and pressure should be used to monitor the process. Each item sterilized should be inspected for damage, packaging material integrity and moisture on removal from the autoclave. Any item found not to be fit for purpose should be removed from the manufacturing area and an investigation performed. | "8.55 For porous cycles (hard goods) time, temperature and pressure should be used to monitor the process. Each item sterilized should be inspected for damage, packaging material integrity and moisture on removal from the autoclave. Any item found not to be fit for purpose should be removed from the manufacturing area and an investigation performed, unless justified by a predefined risk analysis for impact and related root cause identification (e.g. proceduralized decision tree)." | Only atypical damage or moisture should be investigated to identify potential unknowed failure modes, evaluate quality impact and implement appropriate corrective actions.
1245 - 1247 | 8.58 Indicates a guidance value (normally weekly) for leak tests on the sterilizing system, but this and other guidance values in the document should be removed. | "8.58 Leak tests on the sterilizing system should be carried out periodically (normally weekly) when a vacuum phase is part of the cycle or the system is returned, post-sterilization, to a pressure lower than the environment surrounding the sterilized system. The frequency of testing should be based on the principles of QRM." | See General comment 3: Leak testing on system can vary based on the criticality of the sterilizer. At times it should be incorporated into every cycle and in other systems with low risk it could be very infrequent. Because of this, recommend not setting a frequency and leaving this to QRM assessment.
1249 - 1253 | 8.59 The description relating to steam sterilisation requirements is confusing and needs clarification. Air removal is true only for autoclaves for porous loads. It is not technically feasible for SIP's conducted in Compounding systems (e.g. Bowie&Dick test cannot be put in a compounding line). In these cases, the temperature and BI's results can demonstrate a correct sterilization process. The term SIP in this section leads to a misinterpretation. Remove "(normally performed on a daily basis)" and replace with 'performed on a rotine basis' (See general comment 3). 8.59 The placing of items in an autoclave can vary in position and do not normally ensure free draining. The loads are set up to allow the penetration of steam and removal during vacuum pulls to ensure no build up of condensation during the cycle. | '8.59 For porous load cycles, there should be assurance of adequate air removal prior to the sterilisation stage. During validation, this can be demonstrated in each cycle by having a low equilibration time. In routine operation this can be demonstrated using a specific air removal test cycle performed on a routine basis, or an air detector system. Loading patterns should be designed to aid effective air removal and steam penetration into the load and be free draining to prevent the build up of condensate in locations that could compromise load sterilization." | The proposed text provides scientifically correct guidance. If an adequate assurance of air removal prior to and during sterilization is in place, then an air removal test cycle should be performed on a regular basis or an air detector system. Items in an autoclave are positioned and wrapped to ensure proper steam penetration and removal of residual condensate and ensure no condensate build up. They are not necessarily free draining.
1271 | 8.63 added a requirement to keep all systems pressurized after sterilization. This is not technically possible for all systems such as a Lyophiliser, Filling tubing and needles SIPed in an Isolator, disposable systems that part of it is SIPed with the piping or tank, etc. but where other controls and measure are taken to ensure integrity. | "8.63 Where steam in place systems are used (e.g. for fixed pipework, vessels and lyophiliser chambers), the system should be appropriately designed and validated to assure all parts of the system are subjected to the required treatment. The system should be monitored for temperature, pressure and time at appropriate locations during routine use to ensure all areas are effectively and reproducibly sterilized. These locations should be demonstrated as being representative of, and correlated with, the slowest to heat locations during initial and routine validation. Once a system has been sterilized by steam in place, controls or design measures must be in place to prevent loss of system integrity prior to use. " | Not all systems can be held under positive pressure. Examples include Lyophilizers, filling tubing and needles SIPed in an isolator, etc. In addition, some equipment is depressurised (vent filter testing, etc.). In these cases, systems employ vacuum leak tests, pressure hold tests, storage in protective environments (RTP or other connections on tanks). Therefore the requirement must be updated to account for these other controls needed for these situations.
1280 | 8.64 The description of super heated systems sterilisation is confusing. | 'In fluids load cycles where superheated water is used as the heat transfer medium, the water must consistently and reproducibly reach all parts of the load to ensure that sterilising conditions are present throughout the load'. | The proposed text provides scientifically correct guidance The proposed text provides scientifically correct guidance
1286 | 8.65 The description of super heated systems sterilisation is confusing | 'Qualification of the sterilisation of fluids loads in a superheated water autoclave should include temperature mapping of the entire load and heat penetration and reproducibility studies. All parts of the load must heat up uniformly and achieve the desired temperature for the specified time. Routine temperature monitoring probes are ideally located at the worst case positions identified during the qualification process'. | The proposed text provides scientifically correct guidance The proposed text provides scientifically correct guidance
1486-1496 | 8.88 The filtration of very small volumes of solution is not the only case where PUPSIT can add more risks than benefits: suggest to remove the example or add the risk of intervention into the sterile product pathway, which is the most common reason for not performing PUPSIT Clarify what “transport mechanisms” means | (PUPSIT) may not always be possible after sterilization due to process constraints (e.g. the filtration of very small volumes of solution, risk of contamination of the sterile product pathway). In these cases, an alternative approach may be taken providing that a thorough risk assessment has been performed and….. | The implementation and execution of PUPSIT increases process complexity and inherently increases the risk of product contamination – due to the required manipulation of the filter assembly and piping downstream to the sterile filter (i.e. of the sterile product pathway). Data and studies are available to demonstrate that only under the most exceptional circumstances and product characteristics would a marginally damaged filter not be detected as part of the Post-Use filter integrity test. If the probability for the masking of the flaw is null or extremely low, this should be compared with the contamination risk related to the PUPSIT process, and an evaluation made on the most suitable approach to ensure the proper level of process sterility assurance. A sound risk assessment can 1) identify and minimize the risk for filter damaging before use, 2) identify the risk for the product (based on the product characteristics and process parameters) to be capable to plug a flaw, should it be present, to the point that the post-use integrity testing would not detect it (flaw masking), 3) address the risk posed by the additional components and manipulations required for PUSIT, and 4) decide what controls should be taken to prevent, rather than identify, the failure .
1507-1510 | 8.88 iii Propose to remove part of this wording ' such as the potential to alter integrity test values and therefore prevent the detection of a non-integral filter during a post-use filter integrity test.' | iii "The specific product type, including particulate burden and whether there exists any risk of impact on filter integrity values, such as the potential to alter integrity testing values and therefore prevent the detection of a non-integral filter during a post-use filter integrity test. | Removed sentence section describing hypothetical situation.
1655.1656 | 8.111 Clarification is needed on the wording holding times. Clarification of timing product equipment | The sterilization of lyophilizers and associated equipment, (e.g. trays, vial support rings) should be validated and sterile holding times between sterilization cycles appropriately challenged during aseptic process simulations or validated separately. | We want to disconnect sterile holding time validation e.g. storage of equipment under LAF class A from aseptic process simulation, because as consequence the production area is blocked for the holding time study (e.g. up to 5 days) and no production can occur during that time. Therefore separate holding time validation should also be allowed.
1655.1656 | 8.112 Lyophilizers that are manually loaded or unloaded should normally be sterilized before each load. For lyophilizers loaded by automated closed systems or located within systems that exclude operator intervention, the frequency of sterilization should be justified and documented as part of the CCS. Revise the requirement to remove the word "normally" and allow lyophilizers to be sterilized after campaigns of the same product or live biological agent when loading and unloading is done in Grade A. | "Lyophilizers that are manually loaded or unloaded should be sterilized before each load unless the loading and unloading is done in Grade A and the same product or live agent is being manufactured in a campaign. For lyophilizers loaded by automated closed systems or located within systems that exclude operator intervention, the frequency of sterilization should be justified and documented as part of the CCS." | There is little risk of contaminating the lyophiliser when the area surrounding the chamber is Grade A. Additionally, Annex 5 of EU GMP allows lyophilizers to be sterilized in between campaigns rather than each load..
1665.1669 | 8.113 It is not clear how the integrity of the lyophiliser can be maintained during loading/unloading operations, and therefore the following first sentence of this section should be REMOVED "The integrity of the lyophiliser system should be maintained following sterilization and during use. "8.113 Clarification needed: In case of a lyophiliser that is loaded automatically and sterilization is not performed before every load, e.g. when campaigning automatically loaded lyophilizers) 8113 is contradictory – frequency of leak test should be documented, but then at the end of the paragraph it says at the start of every cycle. | 8.113 The filter used to maintain lyophilizer integrity should be sterilized before each use of the system (batch or campaign as appropriate) and its integrity testing results should be part of the batch certification. The frequency of vacuum/leak integrity testing of the chamber should be documented and the maximum permitted leakage of air into the lyophilizer should be specified and checked at the start of every cycle or campaign | Revision of wording provides a more technically accurate requirement and recognises batch and campaign based operations
2026-2031 | 9.33 The last sentence is a separate requirement / expectation than the other sentences in 9.33. For clarification, break this sentence out into a separate requirement for clarity (include a new 9.34). | NEW 9.34 "…..Where monitoring is routinely performed by manufacturing personnel, consideration should be given to periodic monitoring under the supervision of the quality unit." | Ensure requirement is clearly communicated
2033- 2258 | 9.34, 9.35, and 9.36 Terminology harmonisation request: The use of Aseptic Process Simulation and Process Simulation Test. We suggest annex 1 uses the term Aseptic Process Simulation (APS) throughout as far as possible to avoid misunderstandings and drive harmonization across countries, especially as there is currently no glossary term for process simulation test. |  | Drive harmonization in terminology across countries, Especially as MRA US-EU is in place. APS is the preferred acronym.
2162-2170 | 9.40 Elements for APS are listed but there is no accounting for simulation design based on different technologies. Reintroduce wording similar to that in the previous version of the Annex allowing consideration of technologies used when assessing risk and designing APS: | The following text should be added within section 9.40: " Where barrier technologies (RABS, isolators, BFS, etc.) are used in the routine aseptic manufacturing process, the relative risk and unique aspects of these technologies should be taken into consideration when assessing the design of aseptic process simulation tests." | See General Comment 2: For RABS and conventional clean rooms where direct personnel interaction with the line occurs during operations, activities in the background environment could pose a risk to the critical zone, but would pose a lower or negligible risk for a closed isolator (e.g. number of personnel in the background environment). Without wording regarding consideration of technology, all elements of APS become prescriptive, regardless of technology
2209 - 2213 | 9.47 There is no need for conditions similar to visual inspection procedure to detect a microbiological growth. Although this could apply to the initial visual inspection of APS units, the visual inspection procedures are not adequate for intermediate and final readings where microbial growth could appear. | "9.47 On completion of incubation: i. Filled APS units should be inspected by staff, who have been trained and qualified in the visual inspection procedures, under controlled light and background conditions, that facilitate the identification of any microbial contamination." | The new text helps to avoid mis-interpretation. Microbiological contamination does not need the same inspection conditions that routine defect of unit to be detected (e.g. : no need of black or white panel or specific light intensity)
2290 - 2308 | 10.6 Point i. indicates in addition to pulling sterility samples at the beginning, middle, and end of a batch, to also pull samples at a significant intervention (e.g. interventions where the integrity of the barrier is breached (open door)) or an operator intervention into critical zones. This would suggest that any open door and glove intervention into the critical zone would require pulling a sterility sample. | "For products which have been filled aseptically, samples should include containers filled at the beginning, middle and end of the batch. Additional samples should be considered as outlined in the CCS for significant issues (e.g. Major breakdown of the equipment causing repairs, clean up of spills) where the beginning, middle, and end samples may not be representative of the batch. " | The additional sterility samples is not consistent with a QbD approach to create a robust aseptic process. The APS program challenges the ability to successfully conduct inherent and corrective interventions through gloves and with open doors successfully. In addition, these interventions typically occur after automatic clearing of the line and/or result in the manual or automatic rejection of potentially impacted product containers. Therefore these actions eliminate the risk of product impact. In addition, EM monitoring of the critical area and personnel conducting these activities are taken to evaluate any potential impact to product. Therefore, these qualification activities and monitoring activities ensure the quality of the environment is maintained and therefore any additional Sterility samples should be taken only under circumstances which the beginning, middle, and end of batch samples would not be representative of the validated state of the line.
2310 (10.7) | 10.7 There is no discussion about use of rapid methods in lieu of conventional sterility test due to limited product shelf life.. | "For some products it may not be possible to perform a sterility test prior to release because the shelf life of the product is too short to allow completion of a sterility test. In these cases, the CCS should clearly capture the identified risks, the additional considerations of design of the process and additional monitoring and/or alternative test methods required to mitigate the identified risks. " | The proposed revised text enables the option to utilise any rapid sterility test methods that may be developed in the future and helps ensure the longevity of the annex 1.
Glossary | Glossary: There should be a definition of campaign within the glossary
2591 | Glossary (line 2591): Change to 'Unidirectional airflow (UDAF)'
2595 | Glossary (line 2595): Change to 'Unidirectional airflow (UDAF) unit'
322-326 | Proposed New Glossary Term - As working height is mentioned in 4.32 and key for the velocity measurements, request adding a definition for working height and guidance on where to measure. | "Working Height: The horizontal plane that passes through the centre of a defined critical zone (i.e., where product and/or critical surfaces are exposed to the environment). Measurement of working height velocity should be measured approximately 300 mm (12 inches) or more above the working height to obtain a consistent and meaningful reading." | This definition has been taken mainly from the ISPE Baseline Guidance volume 3 2018 on measuring velocities and ties in with ISO and FDA previous guidance. The height is scientifically based and acknowledges that as you near the surface of the machine it can be challenging to get consistent readings of velocity, so provides a recommendations for setting the height.
26-29 (OOS) | Scope: Lines 21-26 "However, some of the principles and guidance, such as contamination control strategy, design of premises, cleanroom classification, qualification, monitoring and personnel gowning, though not compulsory for non-sterile manufacturers, may be used to support the manufacture of other products that are not intended to be sterile such as certain liquids, creams, ointments and low bioburden biological intermediates but where the control and reduction of microbial, particulate, and pyrogen contamination is considered important." | "However, some of the principles and guidance, such as contamination control strategy, design of premises, cleanroom classification, qualification, monitoring and personnel gowning, though not compulsory for non-sterile manufacturers, may be used to support the manufacture of other products that are not intended to be sterile such as certain liquids, creams, ointments and low bioburden biological intermediates but where the control and reduction of microbial, particulate, and pyrogen contamination is considered important." | Inclusion of these statements provides a great deal of uncertainty of expectation of the requirements to Non-sterile products. The governing guidance for contamination control for the manufacture of non-sterile products is provided in the EU Annex 2 regulation. Any annex 1 expectations should be directly cross-linked or contained in Annex 2 to ensure clarity of expectations for non-sterile manufacturing.
231-237 (OOS) | 4.11 The transfer of materials, equipment, and components into an aseptic processing area should be carried out via a unidirectional process. Where possible, items should be sterilized and passed into the area through double-ended sterilizers (e.g. through a double-door autoclave or depyrogenation oven/tunnel) sealed into the wall. Where sterilization on transfer of the items is not possible, a procedure which achieves the same objective of not introducing contaminant should be validated and implemented, (e.g. using an effective transfer disinfection, rapid transfer systems for isolators or, for gaseous or liquid materials, a bacteria-retentive filter). Add: "Where unidirectional flow is not possible, time-based separation of activities (ingress/egress) by procedure should be considered." | 4.11 The transfer of materials, equipment, and components into an aseptic processing area should be carried out via a unidirectional process. Where unidirectional flow is not possible, time-based separation of activities (ingress/egress) by procedure should be considered. Where possible, items should be sterilized and passed into the area through double-ended sterilizers (e.g. through a double-door autoclave or depyrogenation oven/tunnel) sealed into the wall. Where sterilization on transfer of the items is not possible, a procedure which achieves the same objective of not introducing contaminant should be validated and implemented, (e.g. using an effective transfer disinfection, rapid transfer systems for isolators or, for gaseous or liquid materials, a bacteria-retentive filter). | Some existing facilities have limited space and time/based separation to avoid cross contamination is the only option.
252-255 (OOS) | 4.12.i. Personnel airlocks: Areas of increasing cleanliness used for entry of personnel (e.g. from Grade D to Grade C to Grade B). In general hand washing facilities should be provided only in the first stage of the changing room and not be present in changing rooms directly accessing Grade B cleanrooms. Revise last sentence to add "unless required for biosafety when manufacturing immunological medical products." | 4.12.i. Personnel airlocks: Areas of increasing cleanliness used for entry of personnel (e.g. from Grade D to Grade C to Grade B). In general hand washing facilities should be provided only in the first stage of the changing room and not be present in changing rooms directly accessing Grade B cleanrooms unless required for biosafety when manufacturing immunological medical products. | The requirement to not have washing facilities in changing rooms directly accessing Grade B cleanrooms contradicts Annex 5 Manufacture of Immunological Veterinary Medicinal Products 11e which states "changing rooms designed and used as airlocks, and equipped with washing and showering facilities if appropriate."
295-302 (OOS) | 4.15 eliminated the 2017 specific requirement (5.12) that airflows must the visualized for Grade A/B only. 2020 draft indicates that Airflow patterns within cleanrooms and zones must be visualized. | 4.15 Airflow patterns of transitions between classified areas and within critical zones should be visualised to demonstrate that there is no ingress from lower grade to high grade areas and that air does not travel from less clean areas (such as the floor) or over operators or equipment that may transfer contaminant to the higher grade areas. Where air movement is shown to be a risk to the clean area or critical zone, corrective actions, such as design improvement, should be implemented. Airflow pattern studies should be performed both at rest and in operation (e.g., simulating operator interventions). Video recordings of Grade A, and Grade A/B interface, airflow patterns should be retained. The outcome of the air visualisation studies should be considered when establishing the facility's environmental monitoring program. | As written, using the Annex 1 glossary of the definition of Cleanroom, this section would drive airflow pattern testing across all points of all graded areas (A, B, C, D). This would mean multiple camera setups to capture the entire area space. Logically, if it is demonstrated through visualisation and differential pressure that the transition (Grade D to C, Grade C to B, Grade B to A) does not allow ingress to the higher grade area, then there is very low probability that contaminants will pass through to the cleaner area and the added studies are of little benefit. Air flow patterns visualization should not be expected for Grade A, B, C and D regardless of activity and risk for product
304-312 (OOS) | 4.16 "A warning system should be in place to instantly indicate and warn operators of any failure in the air supply or reduction of pressure differentials…" | Suggest to clarify for what grades the instant alarm is mandatory in (Grade A, Grade B and Grade C/D only if critical activities such as filling with BFS or in isolators). | The application of instant warning should be appropriate to risk for product.
524-525 (OOS) | 4.36 The rotation of disinfectants and the periodic use of sporicidal agents is too prescriptive and is an example where the approach can be included in the CCS based upon the criticality of the activities being performed and the associated risk to the product. | Suggest to clarify the guideline for what cleanroom grade the requirement is to be applied. CCS | There are numerous studies showing no added value of rotational use of two different disinfectants. Furthermore, confirmatory studies mentioned in 4.37 must anyway demonstrate appropriateness of the disinfection method. Use of sporicidal agent shall reflect the criticality of activities and risk to product as per the CCS. Not same level/frequency fits all grades. Overuse of sporicides may effect cleanroom equipment more rapidly.
534-540 (OOS) | 4.38 states that disinfectants used in Grade C and D may also be required to be sterile | 4.38 Disinfectants and detergents used in Grade A zone and Grade B areas should be sterile prior to use (disinfectants used in Grade C and D may also be required to be sterile). Where the disinfectants and detergents are made up by the sterile product manufacturer, they should be monitored for microbial contamination. The strategy for disinfectants used in Grade C and D areas should be documented in the contamination control strategy and based on QRM principles. Dilutions should be kept in previously cleaned containers and should only be stored for defined periods. If disinfectants and detergents are supplied "ready-made" then results from certificates of analysis or conformance can be accepted subject to successful completion of the appropriate vendor qualification. | See general comment 1. Clarification is needed to ensure that it is not mandatory that Grade C and D disinfectants are sterile.
572-574 (OOS) | 5.5 - Requirements and guidance for VHP decontamination is missing. It is understood that this is not considered an inherently robust surface sterilization method but a decontamination method and that should be clear in the Annex. But since it is a widely used decontamination method for isolator surfaces , including HEPAs and indirect product contact surfaces a way of recognising this process is needed for this process to identify and mitigate this fragility. | Expand section 5.5 to recognise applications of VHP where it used as the primary surface decontamination method for indirect product contact parts but provide a caveat 'Direct and indirect contact parts should be sterilized. Direct contact parts are those that the product passes through, such as filling needles or pumps. Indirect product contact parts are equipment parts that come into contact with sterilized critical items and components. For indirect product contact parts , where the design prevents off line or in situ sterilisation, a reliable and validated decontamination process should be used. A risk assessment in these cases is required as part of CCS process' | The suggested text draws on examples elsewhere in the annex draft where risk assessments and CCS can be used to identify risks and reduce / eliminate where feasible . ( e.g. manual aseptic manipulations lines 970, 935, ) or where design constraints are evident ( e.g. viewing constraints Line 314 . The reference to risk management and the CCS would acknowledge the design constraint and ensure that this gets continually reviewed as part of residual risk acceptance and the performance of the systems employed to measure the decontamination process in lieu of a sterilisation process .
588-592 (OOS) | 5.9 discusses NVPM probes and codifies the 1m length and it additionally specifies a 15cm (~6 inch) minimum bend radius which hasn't been documented previously. This should actually look at particle path impingement and based on tube diameter...there is an ASTM F50-12 that addresses this, but may not be applicable for all systems and technologies. | 5.9 Particle counters, including sampling tubing, should be qualified. The tubing length should not exceed the manufacturer's recommended length and diameter and should be no greater than 1 meter with a minimum number of bends and bend radius should be greater than 15 cm. Portable particle counters with a short length of tubing should be used for classification purpose. Isokinetic sampling heads should be used in unidirectional airflow systems and should be positioned as close as possible to sample air representative of the critical zone. location. | ISO 14644-1 C.4.1.2 states the use of manufacturer's recommendations for tubing size and length. The proposed wording offers alignment with the language in ISO 14644-1 C.4.1.2 for consistency in interpretation .
695-696 (OOS) | 6.17 Because pure steam systems are self-sterilizing, it is not necessary to sample them for total microbial count as required by the WFI monographs of the relevant Pharmacopoeias. Please make this statement more specific. | Reword to " . . . Steam condensate should meet the current monograph for WFI of the relevant Pharmacopeia, with the exception of microbial count. . . . | It is not necessary to sample pure steam for total microbial count because pure steam systems are self-sterilizing.
721 - 733 (OOS) | Heating and cooling and hydraulic systems 6.21 Major items of equipment associated with hydraulic, heating and cooling systems, e.g. such as those associated with Blow-Fill-Seal equipment should, where possible, be located outside the filling room. Where they are located inside the filling room there should be appropriate controls to contain any spillage and/or cross contamination associated with the hydraulic system fluids. Where possible, the system should be at a lower pressure than the processed fluid. 6.22 Any leaks from these systems that would present a risk to the product should be detectable (i.e.an indication system for leakage). 6.23 For both vacuum and cooling systems there should be periodic cleaning/disinfection as determined in the CCS. Please clarify what other types of heating, cooling, vacuum and hydraulic systems this section would refer to. |  | The scope of the requirement is not clear. The headline is stating Heating and cooling and hydraulic system, Point 6.23 refers to vacuum system…this is somehow unclear. Can you give an example or just clarify.
746-747 (OOS) | 7.3 indicates that Non-essential processes such as product inspection and in process testing should be conducted outside the clean areas wherever possible. | 7.3 Non-essential processes such as product inspection and in process testing should be conducted outside the clean aseptic areas wherever possible, and limited in use within the grade C/D areas to testing where real-time testing and feedback is important to the control strategy and does not present a contamination risk to the process. | There are a number of testing and IPC processes which are very beneficial for real time information and feedback to be completed by operators in the C & D areas and do not adversely impact the area cleanliness. Examples include checking pH real time to verify pH of a solution or product while manufacturing it to adjust if required, Container closure seal tightness checks, etc. This testing ensures timely control to the process, efficiency in the operation, and have not shown to adversely impact the C&D areas.
749-751 (OOS) | "7.4 All personnel including those performing cleaning, maintenance, monitoring and those that access cleanrooms should receive regular training, gowning qualification…" This requirement states that personnel working in grade C and D should go through gowning qualification. Gowning qualification of personnel working with non critical activities in lower grade cleanroom should not have to perform gowning qualification based on the lower risk for the product and the marginal gain of product security by this requirement. If filling is occurring in grade C as for BFS then it should be specified that this is what is meant and that personnel working with other non critical activities are excluded from this requirement. Additionally the regular periodic training may not always cover all the aspects listed. | Re-phrase so that only personnel working in grade A and B and personnel in grade C and D involved in aseptic filling of product should receive gowning qualification. Also state that the elements of training listed are required for new starters but may not all be required during every regular periodic retraining "7.4 All personnel working in the cleanrooms should receive regular training, gowning qualification, and assessment in disciplines relative to the correct manufacture of sterile products......." | This requirement states that personnel working in grade C and D should go through gowning qualification. Gowning qualification of personnel working with non critical activities in lower grade cleanroom should not have to perform gowning qualification based on the lower risk for the product and the marginal gain of product security by this requirement. Aseptic gowning training is covered in section 7.5 so can be removed from 7.4.
779-781 (OOS) | 7.7 states that "There should be systems in place for disqualification of personnel from entry into cleanrooms based on aspects including ongoing assessment and/or identification of an adverse trend from the personnel monitoring program and/or after participation in a failed APS." However the section does not take into account whether or not the personnel were the root cause of the failed APS which should determine whether or not their disqualification is necessary. | 7.7 There should be systems in place for disqualification of personnel from entry into cleanrooms based on aspects including ongoing assessment and/or identification of an adverse trend from the personnel monitoring program and/or after participation in a failed APS where the root cause of the APS failure has been attributed to a person or group. . | All the personnel working in Grade B are not always involved in manufacturing operation or other activities that involve ingress in Grade A or access to process or direct or indirect contact to the process or the product. The need for requalification of personnel for a failed APS should only be if the person or group was determined to be the root cause. In other words, if the root cause of the APS failure is proven to be due to a mechanical fault there is no need to requalify the people.
1124-1126 (OOS) | 8.40 discusses mechanisms in place to detect a sterilization cycle that does not conform to the validated parameters. Any failed sterilization or sterilization that deviated from the validated process (e.g. have longer or shorter phases such as heating cycles) should be investigated. | 8.40 There should be validated mechanisms in place to detect a sterilization cycle that does not conform to the validated parameters, which ensure the sterilization cycle fails preventing forward processing of the load. Failed cycles should be investigated unless justified by a pre-determined risk analysis for impact and known root cause (e.g. Proceduralized decision trees) Any failed sterilization or sterilization that deviated from the validated process (e.g. have longer or shorter phases such as heating cycles) should be investigated. | Request an update to require the use of an upfront QbD approach to detect and prevent forward processing of a load versus the manual review and investigation. This would support the use of automation and proper use of control strategies to support sterilization processes. In the case of investigation criteria, only atypical failure should be investigated to identify potential unknowed failure modes, evaluate quality impact and implement appropriate corrective actions.
1133-1135 (OOS) | 8.41 "BI results in isolation do not give assurance of sterilization and should not be used to override other critical parameters and process design parameters." This is a faulty statement. | Re-phrase so that it is acceptable to base sterility assurance on the results of BI alone, but to make it clear that physical measurement should be performed in conjunction with the use of biological indicators. | This is a faulty statement. BIs can be used alone for sterility assurance if the BI has a minimum D-value of 1 minute and a minimum population of 1 million spores. For instance in product specific sterilisation processes where the calculated physical parameters does not show that sterility is achieved. For instance the dry heat sterilisation of micronised Budesonide used for Pulmicort respules. This process gives a negligible FH-value but sterility is achieved when the Budesonide is heated. Likewise if physical data is missing due to a broken temperature or pressure sensor during qualification or requalification this can be accepted if the BI show a 6 log reduction.
1138-1139 (OOS) | 8.42 "Prior to use of a new batch/lot of BIs, the population and identity of the indicator organism of the batch/lot should be verified." According to Ph Eur and USP, ID is not mandatory to perform ID if you have a qualified audited supplier or unless you have an investigation. Instead USP requires that purity is controlled to assure that there is no contamination. | "Prior to use of a new batch/lot of BIs, the population and purity of the indicator organisms of the batch/lot should be verified." | Harmonise with USP/PhEur
1152-1153 (OOS) | 8.44 States Sterilization records should be available for each sterilization run. Each cycle should have a unique identifier. They should be reviewed and approved as part of the batch certification procedure. Recommending additional text (consistent with comments from 8.40) to allow for the use of QbD approach with validated digital plant concepts automated / AI etc. to support the analysis of the cycles enabling review by exception in the batch certification process. | 8.44 Sterilization records should be available for each sterilization run. Each cycle should have a unique identifier. They Their conformity should be reviewed and approved as part of the batch certification procedure either manually or through a validated automated review process with manual approval (release by exception). | Comments aimed at enabling the use of current and future developments in the use of QbD and automation / AI in the digital plant model to evaluate and prevent forward processing of autoclave cycles not meeting validated parameters. This QbD approach and the use of automation is a reality for our firm and much of industry.
1190-1192 (OOS) | 8.49 The first sentence has been updated from the 2017 version to allow for electronic recording of parameters which is a great change to support the use of data collection and storage systems to support the modern manufacturing plant. A small rewording is suggested. The second sentence of having separate monitoring and recording systems being independent of the controlling system is accurate, but the example of using double probes is not always a suitable example of how this is accomplished. Typically instruments are built fail safe to fail in a state as to not impact the process. Also, identifying a non-compliant cycle is accomplished through multiple instruments (temperature, pressure, liquid sensors in drains, etc.) that ensure a successful validated cycle is run. Recommended this sentence be updated with a requirement on what to accomplish versus how to do it (e.g. dual probes). In addition, as many pharmaceutical companies are working to use automation, AI, and digital plant, allow use of automation to ensure a successful cycle which is more reliable than human manual review. | 8.49 Each heat sterilization cycle should be recorded either electronically or by hardcopy, on equipment with suitable accuracy and precision. All measurements for control and monitoring of parameters that determine a heat sterilization cycles successful adherence to the validated cycle shall be recorded either electronically or by hardcopy recorders, using equipment with suitable accuracy, precision, and sampling frequency. Monitoring and recording systems should be independent of the controlling system (e.g. by the use of duplex/double probes).The system must have safeguards and/or redundancy in its control and monitoring instrumentation to detect a cycle not conforming to the validated cycle parameter requirements and abort or fail this cycle. | The expectation of a modern sterilization process should be a Quality by Design approach which identifies all parameters, phases, times, etc. that are critical to a successful sterilization cycle. The design of the system should have a control strategy such that the alarms and controls that detect and abort a cycle that does not meet the validated cycle. This enables the use of automation (digital plant) to identify a cycle not meeting the parameters versus manual review. In addition, identifying a non-compliant cycle can be accomplished through multiple instruments interacting (temperature, pressure, liquid sensors in drains, etc.) as well as comparisons of temperature and pressure against the saturated steam curves that ensure a successful cycle versus having double temperature probes. Proposed modification sets this QbD expectation to identify the parameters upfront and ensures that the proper safeguards are in place to detect and abort a cycle not meeting a valid cycle. If the change is not accepted, request at least the acknowledgement in the requirement that a QbD approach to accomplish this is possible to allow technology to support these processes as much of industry is working to leverage digital plant, AI and other advanced systems to move away from manual reviews of sterilization reports.
1194-1197 (OOS) | 8.50 Typically, sterilization systems are designed with locations of temperature probes identified during design based on knowledge of locations of the systems needing monitoring. Examples include autoclave chamber temperature, drain or drain line temperatures, etc. The validation activity with heat distribution studies and penetration studies do not therefore determine the location (as the locations are already established), but confirm the positions of the probes are representative of the system. Therefore request update to reflect this. | 8.50 The position of the temperature probes used for controlling and/or recording should be identified during design and determined confirmed as representing the system during the validation which should include heat distribution and penetration study and, where applicable, also checked against a second independent temperature probe located at the same position. | Change to represent that probe positions are not determined during validation, but instead identified during a design and confirmed that the locations of the installed probes in the system are representing the system.
1292 (OOS) | 8.66 The description of dry heat sterilisation is not accurate and confusing | 8.66 Change to 'Dry heat is used for sterilization at temperatures of 160oC or above. The mechanism for microbial kill is different to that associated with steam sterilisation. Dry heat can also be used for depyrogenation (and sterilisation) at temperatures of approximately 230oC or above. Dry heat is often used in the depyrogenation and sterilisation of glass containers and other components used during aseptic filling. The process may be operated in a batch oven or in a continuous tunnel process for glass containers'. The combination of time and temperature ….. | The proposed text provides scientifically correct guidance
1298 - 1316 (OOS) | 8.67 Recommend removing the requirement to visualize depyrogenation tunnel airflow and focus on the differential pressure profile across the zones of the tunnel and other testing (Heat distribution, particle monitoring, etc.). See rationale. | 8.67 Dry heat sterilization/depyrogenation tunnels should be configured to ensure that airflow protects the integrity and performance of the Grade A sterilizing zone by maintaining pressure differentials and airflow through the tunnel from the higher grade area to the lower grade area. Differential pressure profiles should be assessed Airflow patterns should be visualised and correlated with temperature studies. The impact of any airflow change should be assessed to ensure the heating profile is maintained. All air supplied to the tunnel should pass through at least a HEPA filter and periodic tests should be performed to demonstrate air filter integrity (at least biannually). Any tunnel parts that come into contact with sterilized components should be appropriately sterilized or disinfected. Critical process parameters that should be considered during validation and/or routine processing should include, but may not be limited to: i. Belt speed or dwell time within the sterilizing zone. ii. Temperature – minimum and maximum temperatures. iii. Heat penetration of the material/article. iv. Heat distribution/uniformity. v. Airflows determined by differential pressure profiles– correlated with the heat distribution and penetration studies. | The majority of Depyrogenation tunnels preclude the ability to safely and effectively conduct airflow pattern testing (visualization) especially with the tunnel at temperature. Testing must be adapted to the specific processing conditions in the tunnel through differential pressure profiles as well as air quality can be confirmed via particle monitoring and temperature mapping can provide insight into the correct temperature and therefore airflow to confirm sterilization is being conducted effectively.
1298-1301 (OOS) | 8.67 Dry heat sterilization/depyrogenation tunnels should be configured to ensure that airflow protects the integrity and performance of the Grade A sterilizing zone by maintaining pressure differentials and airflow through the tunnel from the higher grade area to the lower grade area. Recommennd to either revise last sentence to section 8.67 to account for the manufacturer of live biological agents (see next column), or to add a general qualifiying statement that accounts for any specific requirements (e.g. airflows) when manufacturing biological agents (rooms, tunnels, ovens, etc.) | Dry heat sterilization/depyrogenation tunnels should be configured to ensure that airflow protects the integrity and performance of the Grade A sterilizing zone by maintaining pressure differentials and airflow through the oven or tunnel from the higher grade area to the lower grade area unless a live biological agent requiring containment is being manufactured. In this case, the oven or tunnel may be negative to the lower grade area. | The statement relating to the airflow protecting the integrity and performance of the grade A sterilising zone is equally applicable to sterilization ovens as it is to sterilization/depyrogrnation tunnels. However, the sentence (lines 1298-1300) does not apply when live biological agents requiring containment are manipulated in the Grade A/B area. In this case, the pressure inside the Grade A sterilizing zone is negative to the pressure of the lower grade area (e.g. the oven or tunnel is designed as pressure bubble for containment) in accordance with Annex 5 of EU GMP.
1318 - 1320 (OOS) | Section 8.68 refer to Fh value for thermal depyrogenation process. For dry heat depyrogenation process Fh is called Fd (Refer to USP<1228-1>) |  | Correct terminology
1324-1325 (OOS) | 8.69 What is meant with "biological measurement"? Endotoxin levels are measured with a special photometer as a change in colour/turbidity. | Clarification needed | Clarification needed
1362 (OOS) | Requirements and guidance for VHP decontamination is missing. It is understood that this is not a sterilization method but a decontamination method and that should be clear in the Annex. But since it is a widely used decontamination method requirements guidance is needed for this process. | Add a section, for VHP decontamination, resembling the section for Sterilization with ethylene oxide but with the clear differentiation that the VHP process is not considered a sterilisation process. | Additional information required to ensure the requirements are clear.
1364 (OOS) | 8.75 Use of ethylene oxide as sterilising agent. The current text does not reflect recent developments in EtO vial supplies | This method should only be used when no other method is practicable. For empty containers intended to be filled with aqueous products, (e.g. prefilled syringes), the need to justify the use of ETO in the sterilisation of the container prior to filling can be waived, as the degradation kinetics of ETO in an aqueous medium have been sufficiently demonstrated. However, the levels of toxic residues (ETO and halogenated ethylenehydrines) in the finished product need to fulfil the requirements of ICH M7... | Harmonisation with current PhEur and "Guideline on the sterilisation of the medicinal product, active substance, excipient and primary container"
1410-1414 (OOS) | 8.82 Describes "a second filtration through a sterile sterilizing grade filter, immediately prior to filling, should be considered as part of an overall CCS" From the text in section 8.82 it is difficult to understand what the requirement is and what the recommendation is and what is good to have. First it is mentioned that bioburden reduction (sterilisation grade filters) may be used at multiple points. This is interpreted as all filters that is used before the final sterile filter before filling. The next part of the sentence is then making a reference to the primary sterile filter which could be one of the previously mentioned or? The section is very hard to understand and interpret. Clarification is needed. | Update based on the clarification…... | Clarification is needed if this is stating that a second sterile filter be added right before filling of the product? With the addition of PUPSIT, the final POUF filter is being confirmed that the POUF integrity is in place and not damaged before and after the filling. If the consideration is to add another redundant POUF, this is further increasing the complexity of the sterile boundary. Recommend that a QRM approach should be the driver for any use of multiple filters.
1482-1484 (OOS) | 8.87 has a "Note" that states "Results of theses checks should be included in the batch record". The assumption is that the "checks" referred to are the filtration process conditions listed in 8.87.iii, but it is unclear. | Note: Checks for filtration process conditions should be included in the batch record. Any significant difference in parameters from those validated to those observed during routine manufacturing should be noted (either by manual review or validated process to detect process conditions not meeting validated parameters) and investigated | Request clarification of the "checks" as relating filtration process conditions to filter validation for batch records/disposition
1515 (OOS) | 8.89 Bracket filter performance by confirmation of beginning a process with an integral filter | " . . By testing on installation and after use, …" | Good quality practice - known state at the start and end of a use
1517-1521 (OOS) | 8.90 "The integrity of non-critical air or gas vent filters should be confirmed and recorded at appropriate intervals. Where gas filters are in place for extended periods such as vent filters, integrity testing should be carried out pre and post-use. The maximum duration of use should be specified and monitored based on risk (e.g. considering the maximum number of uses and sterilization cycles permitted)." Propose to remove the second sentence, highlighting requirement for pre and post-use integrity testing of non-critical gas vent filters. | "The integrity of non-critical air or gas vent filters should be confirmed and recorded at appropriate intervals. Where gas filters are in place for extended periods such as vent filters, the maximum duration of use should be specified and monitored based on risk (e.g. considering the maximum number of uses and sterilization cycles permitted)." | Earlier in the text, it is cited that the integrity of critical gas filters should verified after use. Now in this section, it is written as a requirement that when non-critical gas filters are in place for extended periods, then testing should be both pre and post-use. This is a conflicting message.
1554-1601 (OOS) | 8.97 There is a mix-up between the Form-Fill-Seal process and the Blow-Fill-Seal process. They are two separate techniques that should be addressed separately. Most of the requirement under the heading "Form-Fill-Seal" do not apply to Blow-Fill-Seal. | Remove Blow-fill-seal from the text in lines 1554-1601 and add under Blow-Fill-Seal lines 1602-1643 those requirement from under the section for Form-Fill-Seal that apply also for BFS.
1556 - 1563 (OOS) | 8.97 Update section specifically for VFFS since BFS section starts on line 1602. This will provide more clarity. | 8.97 Form-Fill-Seal (FFS) units include blow moulding from thermoforming from thermoplastic film, typically known as Vertical-Form-Fill-Seal (VFFS). VFFS process is an automated filling process, typically for terminally sterilized products, that may utilize a single or dual web system which constructs the primary container out of a flat roll of thermoplastic film while simultaneously filling the formed bags with product and sealing the filled bags in a continuous process. Formed bags containers are considered to be closed through sealing by fusion and, as such, fall under the requirement to perform 100% integrity testing (refer to paragraph 8.21). | Keep separate section for VFFS since the next section is BFS. Adds confusion to what is needed and what can be supported by BFS
1567 - 1579 (OOS) | 8.99 These list of critical parameters (i-vi) need to be associated with VFFS not BFS. Add VFFS clarification on line 1567 | 8.99 Critical parameters for VFFS include, but are not limited to: | These critical parameters are associated with VFFS not BFS, need clarification since BFS does not have these parameters
1581 (OOS) | 8.100 Seal strength and uniformity applies to VFFS for bag. Add clarification for VFFS. | 8.100 Seal strength and uniformity should be monitored routinely for VFFS. | Seal strength and uniformity applies to VFFS for bag
1609 (OOS) | 8.103 It is important to indicate the difference between open and closed parison machines for clarification. | For shuttle type include (open parison type)… | Align nomenclature with PDA Technical Report No. 77, The Manufacture of Sterile Pharmaceutical Products Using Blow-Fill-Seal Technology
1611-1612 (OOS) | 8.103 Need to clarify that grade A/B gowning does not require personnel monitoring, or provide guidance for expectations regarding Grade A/B gowning in a Grade C background. | The equipment should be installed in at least a Grade C environment, provided that Grade A/B clothing is used. Grade A/B clothing is intended as an additional risk mitigation control and not intended to meet Grade A/B personnel monitoring or trending requirements since personnel operate in a Grade C environment. | Cannot pass Grade A/B gowning (Alert/Action levels) in a Grade C background
1615 - 1618 (OOS) | 8.104 Grade A air supply is defined in the Glossary (lines 2477-2481). This definition indicates that there is no requirement to perform continuous non-viable monitoring. For rotary type equipment with a closed parison it is impossible to perform continuous non viable or viable monitoring to ensure Grade A conditions due to the small space Grade A filling space and the closed parison design. It would provide clarity to distinguish between Grade A air supply vs. Grade A conditions. Additionally, due to the reduced risk associated with the closed parison design, the background environment and the gowning requirements should be commensurate with risk. | 8.104 For rotary-type equipment (closed parison), used for aseptic filling, the filling environment inside the parison should be designed to meet Grade A air supply. Other sterility assurance controls such as monitoring of critical parameters and alarms during each batch and parison support filter integrity testing should be considered. The equipment should be installed in an environment background, using risked based approach such as Grade C background using Grade C clothing and facility design. | Clarification between Grade A air supply vs. Grade A conditions. Risk based approach for the background environment and gowning requirements. This will provide clarification for the differences between the requirements for shuttle type (open parison) and rotary type (closed parison) equipment.
1622-1624 (OOS) | 8.105 It is not clear what is intended by cooling system integrity. Suggest to remove or to provide additional details. | "…..Environmental monitoring should be applied taking into consideration elements such as air-filter configuration, air filter integrity, cooling systems integrity, equipment design and installation." | Clarification
1860-1862 (OOS) | 9.10.iv. references trending with particular attention given to "objectionable organism". | iv. Changes in microbial flora type and numbers and predominance of specific organisms. Particular attention should be given to objectionable atypical organisms or those that can be difficult to control such as spore-forming microorganisms. | Request to replace "objectionable organisms" with "atypical organisms", which is a term widely used in the industry and importantly can reflect changes to the environment.
1869-1873 (OOS) | 9.12 implies that all EM Action limits even for grade C and D require an investigation and exceeding alert limits may require this as well. To be consistent with other section of the Annex 1 (including section 10.10 which focuses on trend analysis) where EM data in the C and D area should be trended versus taking action on a single grade C or D hit, the language should be updated to be consistent with other sections of the document. | 9.12 If action limits are exceeded for the processing areas of Grade A or B, operating procedures should prescribe a root cause investigation, an assessment of the potential impact to product and requirements for corrective and preventive actions. If alert levels are exceeded for the grade A and B areas, operating procedures should prescribe assessment and follow up, which should include consideration of an investigation and/or corrective actions to avoid any further deterioration of the environment. EM performance for the grade C and D areas should be trended and operating procedures should prescribe the assessment and follow up actions based on including when investigation and/or corrective actions should be taken. | Evaluation of EM data for batch release should be QRM based and have direct focus on any excursions in the grade A or B areas where it could directly impact the batch. Evaluation of impact from the grade C and D areas should be based on a review of trends and focus on any adverse trends in these areas that should be addressed, but not part of batch certification. From a QRM standpoint focus must be placed on Alert and Action recoveries in the aseptic areas, and monitoring and acting on trends in grade C and D areas.
1915 (OOS) | 9.17 It is stated that a suitable sampling rate to be used for monitoring of non viable airborne contamination so all interventions, transient events and system deterioration can be detected. The sampling rate is therefore typically 28.3 l (1ft3) /min and the guide recommends that the (reduced) monitoring volumes are frequently correlated with the per m3 limits shown in Table 6. However, if the per ft3 limits (and alarms) have been proportioned directly with the per m3 limits, the airborne particle counts would inherently comply with the limits specified in Table 6 without the requirement for formal correlation of each individual sample result. | Change to '..the sampling volume utilised and associated limits should correlate with the limits for the m3 sampling volumes shown in Table 6'. | Continuous 1 minute (1 ft3) sampling with appropriate limit values has been shown ref to be effective in detecting any excursions with inherent correlation with the specified m3 airborne concentrations. Ref Eaton T. Annex 1 of the EC Guide to Good Manufacturing Practice (EC GGMP) and continuous particle monitoring - friend or foe of cleanroom manufacturing? European Journal of Parenteral and Pharmaceutical Sciences 2007; 12 (2): 29-37
1962-1965 (OOS) | 9.25 It is unclear what is intended by the statement that “Particular consideration should be given”. It is unclear whether the intent is to include exit monitoring for all personnel regardless of activity or whether “particular consideration should be given” to those individuals performing critical interventions or activities that pose a higher risk to the process. A requirement to monitor all personnel entering the aseptic area in exit also introduces risk by requiring additional personnel for sampling and additional media to be present within the aseptic area. It would be beneficial to have a risk assessment that evaluates personnel who perform critical interventions and other personnel performing other activities to determine the locations and frequency of personnel monitoring (e.g. immediately after a critical intervention or upon exit from the cleanroom). The personnel monitoring, locations and frequency should be commensurate with the potential risk to the product. | Monitoring should include sampling of personnel at periodic intervals during the process. Sampling of personnel should be performed in such a way that it will not compromise the process. Particular consideration should be given to monitoring personnel following involvement in critical interventions and on each exit from the Grade B cleanroom. A risk assessment should evaluate the locations and frequency of personnel monitoring based on the activities performed and the proximity to critical zones to ensure sampling of personnel does not compromise the process. | Clarification
1974-1979 (OOS) | 9.27 There are a significant differences between a standard clean room (grade A/B ) and isolator (Grade A/ D) , from the point of view of contamination risk. Isolators are closed systems where there is no direct contact with personnel. Furthermore conduct continuous viable monitoring in an isolator represents more risk for the aseptic process than an advantage due to the manipulation during aseptic process. | 9.27. In a conventional cleanroom a continuous viable monitoring in grade A zone (e.g. air sampling or settle plates) should be undertaken for the full duration of critical processing, including equipment (aseptic set-up) assembly & filling operations A similar approach should be considered for Grade B cleanrooms based on the risk of impact on the aseptic processing. The monitoring should be performed in such a way that all interventions, transient events and any system deterioration would be captured and any risk caused by interventions of the monitoring operations is avoided. In case of isolators, closed systems, the microbiological monitoring frequency can be reduced based on a risk assessment (e.g. to once a day) | See general comment 2 <1116> USP recommends a frequency of sampling in isolator of one per day. Continuous monitoring in an isolator is not necessary and can be more of a risk than an advantage.
2014 - 2019 (OOS) | 9.31 Indicates that Consideration should be given to identification of EM excursions in the C&D area. Proposing as these areas should be evaluated from a trend standpoint. Consistent with the comment for 9.12, the decision to identify excursions from trends in these areas. Accepting that ID must always be performed in grade A/B has the consequence that alternative rapid methods that can give a real time result but not ID cannot substitute the traditional methods. However, from a root cause investigation point of view the time of the contaminaiton is of higher significance than the ID. This paragraph should be softened to allow new real time methods and only requesting ID, if possible - and in case of repeated contaminations. | 9.31 Microorganisms detected in the critical processing Grade A zone and immediately adjacent Grade B area should be identified to species level and the potential impact of such microorganisms on product quality (for each batch implicated) and overall state of control should be evaluated. For other grade B areas, the identification of the micro-organism recovered should be done on representative colonies. Consideration should also be given to the identification of microorganisms detected during trend analysis in Grade C and D areas (for example where action limits or alert levels are exceeded or where atypical or potentially objectionable microorganisms are recovered). The approach to organism identification and investigation should be defined in the CCS and proceduralized documented. Use of alternative rapid microiological methods which will give real time results but cannot support identification to species level should be possible if supported by risk assessment. | See general comment 1: A QRM approach needs to be used to determine when identification and investigation is required. Grade A areas and immediate adjacent areas that present the greatest risk of batch impact must be evaluated. Other Grade B areas not near the process require consideration of ID of organisms detected in the environment. Evaluation of impact from the grade C and D areas should be based on a review of trends and focus on any adverse trends in these areas that should be considered for the batch certification. From a QRM standpoint focus must be placed on Alert and Action recoveries in the aseptic areas, and monitoring and acting on trends in grade C and D areas. Accepting that ID must always be performed in grade A/B has the consequence that alternative rapid methods that can give a real time result but not ID cannot substitute the traditional methods. However, from a root cause investigation point of view the time of the contaminaiton is of higher significance than the ID. This paragraph should be softened to allow new real time methods and only requesting ID, if possible - and in case of repeated contaminations.
2078-2081 (OOS) | In 9.35, it is unclear the difference between the two APS lyophilisation points "Replicating the maximum interval between sterilization of the lyophiliser and its use" and "Replicating the maximum period of time between sterilization and lyophilisation" | Request clarification on the difference between the two requirements | Appear to be the same statement
2146-2154 (OOS) | 9.38 Part xii indicates that end of campaign APS can be used for additional assurance or investigative purposes. Request clarification of this requirement and consideration for change to allow this for part of the routine APS qualification with proper justification that it represents all manufacturing activities. | xii. Where campaign manufacturing occurs, such as in the use of Barrier Technologies or manufacture of sterile active substances, consideration should be given to designing and performing the process simulation so that it simulates the risks associated with both the beginning and the end of the campaign and demonstrating that the campaign duration does not pose any risk. The performance of "end of production or campaign APS" may be used as additional assurance or investigative purposes; however, their use should be justified in the CCS or APS strategy and should not replace routine APS. If used, it should be demonstrated that any residual product does not negatively impact the recovery of any potential microbial contamination. | Typically for isolators a well designed end of campaign APS (last batch in the campaign be run with media) captures all campaign activities including set up, full duration of the campaign, and end of campaign activities and fully challenges the aseptic process while minimizing impact to capacity to support ensuring drug supply. This approach must be well designed and justified, and if done, should be a valid method of conducting an APS.
2243-2244 (OOS) | 9.50 Clarification is needed if this is indicating that the failed qualification is the APS and the operator was the root cause or if this is referring to a failed gowning qualification. If it was determined the operator was the root case, would expect that the operator cease working in the area until retraining and qualification (as appropriate) was completed. | 9.50 Where results indicate that an operator may have failed qualification, actions to limit the operator’s activities, until retrained and requalified, should be taken. (Please add additional detail to clarify which qualification - Gowning or APS) | Unclear as to which qualification is failed by the operator that is being referred to. If this is gowning related, this is redundant with section 7.7 and possibly could be changed. If this is APS related, the requirement needs to be more clear that the operator would need to have been the likely root cause and consider removing operator from work in the area until training and requalification is completed.
2275 (OOS) | 10.3 - Unclear on intent of "Where overkill sterilization parameters are set for terminally sterilized products, bioburden should be monitored at suitable scheduled intervals." |  | Clarify intent of this statement since line 2270 indicates must be on each batch.